## Sheet1
Model | CAO-50KW100KWH
PV Data
Max. PV Array Power | 100 kW
Max. DC Voltage | 1000VDC
MPPT Voltage Range | 150~950VDC
Start-up Voltage | 125VDC
Max. Input Current / Sring | 8*20ADC
Isc PV (Absolute Maximum) / Sring | 8*30ADC
No.of MPPT Tracker / Strings | 4/2+2+2+2
Battery Data
Cell Type | LiFePO4
Nominal Capacity | 314AH
Charge Ratio | 0.5C
Energy | 100.5kWh
Nominal Voltage | 320V
Voltage Range | 304-336V
Inverter Input/output(Grid)
Rated Power AC Side (output) | 50KW
Rated Power AC Side (input) | 138kW
Rated Voltage | 380/400VAC， 50/60Hz
Switch Time | <20mS
Max. Continuous Current (input/output) | 200A/ 80A
Max. Output Overcurrent Current Protection | 108A
AC OUTPUT | <2% (Rated Power)
Rated Output Voltage | 380/400VAC，3W+N+PE 50/60Hz
Rated Output Active Power | 50kW
Rated Output Apparent Power | 50kVA
Rated Output Current | 72A
Overload Capacity (off grid) | 110% 30S/120% 10S/ 150% 0.2S
Functional Features
Insulation Monitoring | Yes
Residual Current Monitoring | Yes
Residual Current (RCD) Detection | Yes
Earth Fault Detection | Yes
Ground Fault Current Monitoring | Yes
MPPT Efficiency | 99.9%
Euro / Max. Efficiency | 97.5%/ 98.5%
Display | LED+APP
Charge Equalization Function | YES
System Data
Communication Interface | RS485/WiFi/CAN/DRM(Optional:Bluetooth/LAN/Meter)
System Communication Protocol | Standard: Modbus (Optional)
Protection Function | Over-Charge, Over-Discharge, Over-Current, Short-Circuit, Over-Voltage,Under-Voltage, Over-High/Low Temperature
Enclosure Protection Rating | IP65
Operating Temperature | Charging: 0℃~60℃ ; Discharging: -20℃~60℃
Storage Temperature | -30℃~60℃
Storage Humidity | ≤100% RH
Cycle Life | ≥8000 Cycles@80%DOD & 0.5C，25℃
Life Time | 10 Year
Anti-Corrosion Grade | C4
Battery Temperature Control Method | Industrial Grade Air Conditioning
Cooling | Air Cooling
Firefighting Program | Pack Aerosol + Sevoflurane + Water Fire Interface
DIESEL GENERATOR AUTO Control System | YES
Lighting Protection | YES
Smoke Detector | Optional
Fire Extinguish System | YES
Fire Sprinkler System | YES
Assembly Style | Rack Style (Inverter side hanging)
Cloud Monitoring Platform | YES
Thermal Management AC | YES
Size | 1600*710*1500mm
Weight | Approx.1.1t
Certification | CE-EMC,UN38.3, CEI 0-21, EN50549-1, VDE-AR-N4105, UNE 217002, NTSTYPEA, G99, AS/NZS4777.2